## Installation, Operation & Diagnostics

for the

PE202T-N

#### Pony Express Modem Module

TABLE of CONTENTS

- STANDARDS	Page 2

- PRODUCT OVERVIEW	Page 3

- GENERAL PRODUCT SPECIFICATIONS	Page 4

- MODEM SPECIFICATIONS	Page 5

- ANALOG LINE SPECIFICATIONS	Page 7

- ANALOG MICROWAVE SPECIFICATIONS	Page 8

- CONNECTOR PIN-OUTS	Page 10

- DIP SWITCH FUNCTIONS	Page 11

- MODEM CONFIGURATION	Page 13

- OUTLINE DRAWING	Page 14

- DIAGNOSTICS	Page 15

1.    STANDARDS

Meets FCC Rules Part J, Subpart 15, Class A for radiated emissions.

2.       PRODUCT OVERVIEW

The PE202T Modem Module is an industrial grade Bell 202T modem for connection to unconditioned and conditioned, voice grade, type 3002 two or four-wire leased lines and metallic conductors (eg; pilot wires). It is powered from 5.5 to 9VDC unregulated or +5VDC regulated, is surge protected on the analog and digital connections, and will operate in temperatures from -40 to +85 deg C.

The PE202T module is supplied to OEMs for integration into relays, controllers, RTUs, etc.  The data interface can be either RS232 or TTL.

The PE202T is also at the heart of all Telenetics Bell 202T end-user products such as the MIU202T standalone modem and the Myriad MDR/PE202T rack mount modem bank.

3.    GENERAL PRODUCT SPECIFICATIONS

Dimensions:	 See Section 10

Voltage Supply, Data Interface & Current Requirements:

| Model No. | Voltage | Data Interface | Current |
| --- | --- | --- | --- |
| PE202T-N0 | +5.5 to 9VDC | RS232 | 47 mA |
| PE202T-N1 | +5.5 to 9VDC | TTL | 28 mA |
| PE202T-N2 | +5VDC  5% | RS232 | 47 mA |
| PE202T-N4 | +5VDC  5% | TTL | 28 mA |

Surge Protection:	Analog Line:	3.75kVAC

Digital Line:	ESD ± 10kV

Operating Temperature:		-40 to +85 deg C

Operating Humidity:		0 to 90% (non-condensing.)

Storage Temperature:		-55 to 100 deg C

4.     MODEM SPECIFICATIONS

Modulation:	Bell202T

Modulation Type:	FSK

Synch/Async:	Asynchronous Only

Data Rate:	0 – 1200bps

Transmit Frequency:	Mark:	1200Hz

Space:	2200Hz

Error Correction:	None

Data Compression:	None

Data Modulation Connectivity:	Using 16ms Polling Test

99.999% or better at -37dBm

99.5% or better at -40dBm

95% or better at -43dBm

Serial Formats and Flow Control:

Asynchronous and RTS/CTS flow control

### Analog Interface

Tx Output Level:	-0 dBm or  -10 dBm *

Rx Sensitivity:	-43dBm or  -33dBm *

-43dBm for constant carrier

-40dBm for polling carrier

Line Termination:	Dip Switch Selectable *

Line Impedance:	600 ohms balanced

2 or 4 Wire Configuration:	Dip Switch Selectable *

Other Features

Receiver Equalization:	Compromise Equalization

Self Test Diagnostics:	None

Local Analog Loopback:	See Section 13

Local Digital Loopback:	See Section 13

Remote Analog Loopback	See Section 13

Remote Digital Loopback	See Section 13

Anti-Streaming:	OFF or 45 Seconds (+ 5 sec) *

RTS/CTS delay:	1ms, 12ms, 35ms or 50ms (+5%) *

Note: Soft Carrier will affect RTS/CTS delay time (see Dip Switch Settings ~ Section 9)

Constant Carrier	Switch Selectable  ON or OFF *

Soft Carrier Turn Off	20ms of  900Hz after RTS is turned Off

Carrier Turn ON/OFF	8ms +0.5ms

* Dip Switch Selectable ~ See Section 9

5.   ANALOG LINE SPECIFICATIONS

The PE202T contains analog circuitry for connection to the public conditioned or unconditioned, Bell type 3002, 2 or 4-wire, full duplex voice grade or metallic lines (eg; pilot wires).  The PE202T will also interface to Power Line Carrier or Microwave radio voice channel networks.

The PE202T has an RJ-11 terminated connector.  The following lists the PE202T analog interfaces

Analog Line Type:

Conditioned or unconditioned, Bell type 3002, 2 or 4-wire, full duplex voice grade or metallic lines or better.

Analog Line Specifications:

Bandwidth	300 Hz to 3400 Hz (3dB)

Impedance	600 / 900 ohms , balanced

Frequency Response	400 to 3000Hz (2dB)

Receiver Input Level	-16dBm max.

Output Level	+7 dBm

Noise Signal Level	-48 dBmO

6.   ANALOG MICROWAVE INTERFACE

The PE202Tis designed to interface to a Microwave radio voice channel network with the following specifications:

Phase Jitter (10 to 300Hz)1 degree peak-to-peak, max.

Frequency Response:	300 - 3400Hz -3, +0.7 dB

400 - 3000Hz -1, +0.7 dB

600 - 2400Hz + 0.7 dB

Frequency Stability:	With Synchronization	0.1Hz

Without Synchronization	0.5 Hz / month

Level Stability (w/o regulation):  + 0.5 dB (6 months)

Harmonic Distortion:	1% max, 0.3 % typical

(1Khz, 0 dBmO test tone)

Absolute Delay:	Option – 001:	1500 sec, maximum

Option – 002:	1900 sec, maximum

Group Delay (option - 001):	600 - 3200 Hz 1200 sec, maximum

800 - 2800 Hz 550 sec, maximum

1000-2600 Hz 350 sec, maximum

Group Delay (option - 002):	600 - 3200 Hz with 1000 sec, maximum

800 - 2800 Hz with 400 sec, maximum

1000-2600 Hz with 180 sec, maximum

Linearity:	0.3 dB +3.5 dBmO

Limiting:	+7.5dBmO, max (+6.5 dBmO typical)

for +20dBmO input

Crosstalk (intelligible)(1KhZ test tone at 0 dBmO):

Inter-channel	65 dBmO maximum, 80 dBmO typical

Intra-channel	70 dBmO maximum

Crosstalk (unintelligible):

Adjacent channel	28dBrnc0 maximum (24 455B weighted noise at 0 dBmO   dBrnc0 typical).

Intra-channel 		28 dBrnc0, maximum (18 dBrnc0, typical)

(1KHz test tone at 0 dBmO)

Out of Band Signalling:	Frequency 3825 Hz

Level -20 dBmO

Pulse speed (30 to 80% break) 8 to 14 pps

Pulse distortion +3 dB, level var. 3% max.

Signaling leak -60 dBmO, maximum

- CONNECTOR PIN-OUTS

### Connecting Power to your PE202T

The DC supply voltage is connected to Pins 1 & 6 of the 10-pin header. With your PE evaluation unit you have a ribbon cable to connect the header to a DB9 connector. The two flying leads are connected to header Pins 1 & 6 for power connection

| Pin 10 CD | Pin 5 DSR |
| --- | --- |
| Pin 9 RxD | Pin 4 RTS |
| Pin 8 RxD | Pin 3 CTS |
| Pin 7 DTR | Pin 2 RI Pin 1 |
| Pin 6 Ground | Pin 1 + Power |

8.    DIP SWITCH FUNCTIONS

Table 1

| Switch | Function | ON | OFF |
| --- | --- | --- | --- |
| Switch 1 Switch 1 | Transmit Analog (TxA) Signal Level | 0 dBm | -10 dBm |
| Switch 2 | Anti-Streaming | 45 secs | OFF |
| Switch 3 | Received Analog (RxA) Signal Level | -33 dBm | -43 dBm |
| Switch 4 | RTS/CTS Delay | See Table 2 |  |
| Switch 5 | RTS/CTS Delay | See Table 2 |  |
| Switch 6 | Switched/Constant Carrier | Constant Carrier | Switched Carrier (Follows RTS State) |
| Switch 7 | 2 or 4- Wire Selection | 2-Wire | 4-Wire |
| Switch 8 | Line Termination | 600 ohms | None (22kohms) |
| Switch 9 | Soft Carrier (900Hz) Turn Off | ON | OFF |
| Switch 10 | Spare |  |  |

### Table 2: RTS/CTS Delay Time

| 2 Wire | 4 Wire | Switched Carrier | Constant Carrier | Switch 4 | Switch 5 | Switch 9 Soft Carrier | RTS/CTS Delay Time |
| --- | --- | --- | --- | --- | --- | --- | --- |
| NO | YES | YES | YES | ON | ON | OFF | 50 ms |
| YES | NO | YES | NO | ON | ON | ON | 50 ms |
| NO | YES | YES | NO | ON | ON | ON | 50 ms |
| YES | NO | YES | NO | ON | ON | OFF | 50 ms |
| NO | YES | YES | YES | OFF | ON | OFF | 35 ms |
| NO | YES | YES | NO | OFF | ON | ON | 55 ms |
| YES | NO | YES | NO | OFF | ON | ON | 35 ms |
| YES | NO | YES | NO | OFF | ON | OFF | 35 ms |
| NO | YES | YES | YES | ON | OFF | OFF | 12 ms |
| NO | YES | YES | NO | ON | OFF | ON | 35 ms |
| YES | NO | YES | NO | ON | OFF | ON | 12 ms |
| YES | NO | YES | NO | ON | OFF | OFF | 12 ms |
| NO | YES | NO | YES | OFF | OFF | OFF | 1 ms |
| NO | YES | YES | NO | OFF | OFF | OFF | 12 ms |
| NO | YES | YES | NO | OFF | OFF | ON | 32 ms |
| YES | NO | YES | NO | OFF | OFF | OFF | 1 ms |
| YES | NO | YES | NO | OFF | OFF | ON | 1 ms |

9.   MODEM CONFIGURATION

The following table provides the Dip Switch settings required for most modem application configurations:

|  | Dip Switch Setting |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| 4-Wire Point-to-Point | ON |  | ON |  |  | ON |  | ON |  |
| 4-Wire Multi-Point Master | ON |  | ON |  |  | ON |  | ON |  |
| 4-Wire Multi-Point Slave Rx Term. OFF | ON | ON | ON | ON |  |  |  |  | ON |
| 4-Wire Multi-Point Slave Rx Term. ON | ON | ON | ON | ON |  |  |  | ON | ON |
| 2-Wire Point-to-Point | ON | ON | ON | ON |  |  | ON | ON | ON |
| 2-Wire Multi-Point Master Line Term. ON | ON | ON | ON |  | ON |  | ON | ON | ON |
| 2-Wire Multi-Point Slave Line Term. ON | ON | ON | ON |  | ON |  | ON | ON | ON |
| 2-Wire Multi-Point Slave Line Term. OFF | ON | ON | ON |  | ON |  | ON |  | ON |

For clarity, a blank space = OFF

10.   OUTLINE DRAWING

11.     DIAGNOSTICS

The following pages provide hardware techniques for diagnosing communication problems and thereby isolating the problem at the local modem, the remote modem or the interconnecting line.

(a)	LOCAL ANALOG LOOPBACK (Figure 2)

Requires a loop back cable with a built-in circuit for line loss to simulate a typical leased line condition  (See Figure 3).

Connect the loop back cable to the RJ11 connector on the modem under test.

Set Dip Switches as follows…

Switch 7 = OFF	4-Wire

Switch 9 = ON		Soft Carrier Turn Off Enabled

Switch 1 = ON		Transmit (TxA) Signal Level = 0dBm

Switch 3 = ON		Receive (RxA) Signal Level = –33dBm

Switch 6 = OFF	Switched Carrier

Switch 4&5 = ON	RTS/CTS Delay = 50ms

Test 1:	RTS/CTS Analog Control

Set RTS “ON” and check that CD (Carrier Detect) turns “ON”.

Turn RTS “OFF” and ensure that CD turns “OFF”

With RTS “ON”, run a test message at TxD and verify that the same message is received at RxD with no data errors.

Test 2:	Transmit Signal Power & Receive Levels

Set Dip Switch 1 OFF (TxA = -10dBm)

CD will be OFF.

Change Dip Switch 1 to ON (TxA = 0dBm)

CD should now be ON.

Test 3:	Received Signal Level

Set Dip Switch 1 OFF (TxA = -10dBm) and Dip Switch 3 OFF (RxA = -43dBm).

CD will be ON.

Run a test message at TxD and verify that the same message is received at RxD with no data errors.

Test 4:	Repeat Test 3 for various RTS/CTS delay times and with soft carrier ON and OFF.

(b)	LOCAL DIGITAL LOOPBACK – 4/Wire Network (Figure 4)

On the modem under test, connect TxD to RxD

Switch 1 = ON (TxA = 0dBm)

Switch 3 = ON (RxA = -33dBm)

Switch 4 = OFF (RTS/CTS = 35ms)

Switch 5 = ON   (RTS/CTS = 35ms)

Switch 6 = ON (Constant Carrier mode).

Switch 7 = OFF (4-Wire)

Switch 8 = ON (Line Termination = 600 ohms)

Switch 9 = ON (Soft Carrier = ON)

Transmit a test message from a remote modem and confirm that the same message is received back at RxD on the remote modem with no data errors.

- REMOTE DIGITAL LOOPBACK – 4/Wire Network (Figure 5)

Configure both the local and remote modems as follows:

Switch 1 = ON (TxA = 0dBm)

Switch 3 = ON (RxA = -33dBm)

Switch 4 = OFF (RTS/CTS = 35ms)

Switch 5 = ON   (RTS/CTS = 35ms)

Switch 6 = ON (Constant Carrier mode).

Switch 7 = OFF (4-Wire)

Switch 8 = ON (Line Termination = 600 ohms)

Switch 9 = ON (Soft Carrier Turn Off = ON)

Connect TxD to RxD at the remote modem.

Transmit a test message from the local modem and confirm that the same message is received back at RxD on the local modem with no data errors.

- LINE DIAGNOSTICS

(i) Typical modem configuration for 4-wire Point-to-Point system…

Switch 1 = ON (TxA = 0dBm)

Switch 3 = ON (RxA = -33dBm)

Switch 4 = OFF (RTS/CTS = 1ms)

Switch 5 = OFF (RTS/CTS = 1ms)

Switch 6 = ON (Constant Carrier mode).

Switch 7 = OFF (4-Wire)

Switch 8 = ON (Line Termination = 600 ohms)

Switch 9 = OFF (Soft Carrier = OFF)

(ii) Typical modem configuration for 4-wire Multi-Point system…

Switch 1 = ON (TxA = 0dBm)

Switch 3 = ON (RxA = -33dBm)

Switch 4 = OFF (RTS/CTS = 1ms)

Switch 5 = OFF (RTS/CTS = 1ms)

Switch 6 = ON (Constant Carrier mode).

Switch 7 = OFF (4-Wire)

Switch 8 = ON (Line Termination = 600 ohms)

Switch 9 = OFF (Soft Carrier = OFF)

Adjustments…

In a network with high line loss (greater than 16dB) change Switch 3 (RxA) to OFF (-43dBm).

If there are conditions that can cause cross-talk (TxA leaking into RxA path) set Switch 1 (TxA) to OFF (-10dBm).

Note that noise level should be –50dBm or lower for most FSK operation (signal-to-noise ratio of 15dB or higher)